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FireProtect 2 AC  Heat/CO
EN
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2018

Jeweller
Grade D1
BS 5839
part 6

Wireless mains-powered fire detector with heat and CO sensors


Accurate fire detection-


Heat sensor	CO sensor


· 	Two A1R-class thermistors are located outside the enclosure to eliminate detection delays
· Alarms when the temperature increases by 10°C within a minute or exceeds +64°C
· 
Accurately detects the CO level for up to 10 years

· 	Warns when concentration reaches the dangerous level of 50 ppm, before the first signs of poisoning occur



[image: ]Power supply

The detector is powered by 110-240 V~ mains and includes a sealed backup battery. Even in a power outage, the detector continues to operate, ensuring quick and reliable fire detection throughout its 10-year lifespan.
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AC detectors can synchronously notify of a fire alarm through primary (via Ajax hub) and fallback (detector-to-detector) interconnections. In case of alarm, the hub activates the primary interconnection in 20 s. All information is instantly available
[image: ]in Ajax apps: initiating detector's location, fire alarm type, and exact time. Meanwhile, the initiating detector activates the fallback interconnection. Even if the connection with the hub is lost, raising the interconnected alarm takes only a minute.Fire alarm!
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System supervision	Additional features-
CB




· Regular polling of each system device to display current statuses in apps
· 	Automatic detector self-diagnosis with state reporting to the hub
· Up to 1,700 m of wireless communication and twice as much with a range extender
· Instant maintenance notifications
· 
Automation scenarios activation

· Visual alarm verification using MotionCam detectors or any NVR camera
· Indoor/outdoor intrusion sirens activation

· Alarm delivery to CMS

· Built-in 85 dB siren

· LED indication of detector states



Quick installation and setup

· SmartBracket panel to mount the device without disassembling the enclosure

· Removable WAGO 221 connectors to secure the wires without a screwdriver

· A lock to secure the device on SmartBracket

· Pairing with a hub via QR code, with remote control and configuration in the app




Superior, Fibra, and Baseline product lines are mutually compatible. This opens up numerous possibilities for building systems of any configuration.




	Compliance
	
Compatibility
	Communication with hub
	Power supply

	EN 54-5:2017+A 1:2018
EN 50291-1:2018
	Hubs
Hub Plus, Hub 2 (2G), Hub 2 (4G),
	Jeweller communication technology
	Main
110-240 V~, 50/60 Hz

	BS 5839 (part 6, grade D1)
	Hub 2 Plus, Hub Hybrid (2G),
	
	Up to 2 W of mains power

	
	Hub Hybrid (4G)
	Frequency bands
	consumption

	
	
	866.0-866.5 MHz
	

	
	Range extenders
	868.0-868.6 MHz
	Backup battery

	
	Rex, Rex 2
	868.7-869.2 MHz
	1 x CR 2/3 AA

	
	
	905.0-926.5 MHz
	Sealed

	
	
	915.85-926.5 MHz
	

	
	
	921.0-922.0 MHz
	

	
	
	Depends on the sales region
	

	
	
	Communication range
	

	
	
	up to 1,700 m
	

	
	
	In an open space
	

	Installation
	Enclosure
	Complete set
	

	Operating temperature range
from 0°C to +50°C

Operating humidity
up to 80%
	Colour
black, white

Dimensions
122 x 122 x 54 mm

Weight
305 g
	FireProtect 2 AC (Heat/CO) Jeweller
SmartBracket mounting panel
1 x CR 2/3 AA battery (sealed)
2 x WAGO 221-3 connector (pre-instaIled)
Installation kit Quick start guide
	







For	detailed information, scan the QR code or follow the link:-[!]
•


ajax.systems/support/devices/fireprotect-2-ac-heat-co/


Iii	support@ajax.systems
◄	@AjaxSystemsSupport_Bot
(ill)	ajax.systems
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